## Sayfa1
HOSPITAL COGENERATION SYSTEM ANNUAL SAVINGS ANALYSIS TABLE
Natural Gas Unit Price (TL/m3) | 10.17 |  | Electrical Capacity (kW) |  |  |  |  | 206 |  | Working Hour Periods
Electrik Unit Price (TL/kWh) | 3.78 |  | Thermal Energy Capacity (kW) |  |  |  |  | 246 |  | T1 (06-17) | 320
Exchange Rate (USD/TL) | 20 |  | Fuel Consumption (kW) |  |  |  |  | 495 |  | T2 (17-22) | 140
Calorific Value of Natural Gas (kcal/m3) | 8250 |  | Working Hour |  |  |  |  | 690 |  | T3 (22-06) | 230
Correction Factor for Natural Gas | 0.0011628
| January | February | March | April | May | June | July | August | September | October | November | December | Total
Electric Consumption (kWh/Month) | 127929.8891 | 102663.2834 | 131908 | 116119.3813 | 123625.5326 | 143692.7855 | 138567.7417 | 154249.541 | 145153.0314 | 134998.6169 | 132984.8394 | 104899.9883 | 1556792.6305
Natural Gas Consumption (m3/Month) | 17564 | 15501.5935 | 14590.4476 | 13560.6778 | 8503.7894 | 5155.873 | 4489.4291 | 4980.1233 | 6566.7443 | 6990.3497 | 9313.9438 | 9607.5289 | 116824.5004
Heating Energy Demand (kWh/Month) | 168491.8605 | 148707.1465 | 139966.5028 | 130087.8976 | 81577.0497 | 49460.4096 | 43067.198 | 47774.439 | 62994.9307 | 67058.5874 | 89348.8792 | 92165.2478 | 1120700.149
Electricity Cost (TL/Month) | 483574.9809 | 388067.2112 | 498612.24 | 438931.2613 | 467304.5132 | 543158.729 | 523786.0636 | 583063.2651 | 548678.4586 | 510294.7718 | 502682.6928 | 396521.9558 | 5884676.1435
Natural Gas Cost (TL/Month) | 178625.88 | 157651.2055 | 148384.8517 | 137912.0934 | 86483.5385 | 52435.2285 | 45657.4943 | 50647.8544 | 66783.7894 | 71091.8567 | 94722.8082 | 97708.5685 | 1188105.1688
Total Energy Cost (TL/Month) | 662200.8609 | 545718.4167 | 646997.0917 | 576843.3546 | 553788.0517 | 595593.9575 | 569443.5579 | 633711.1195 | 615462.248 | 581386.6285 | 597405.501 | 494230.5242 | 7072781.3123
Average Power Taken at 06-17 Hours (kW) | 217.383 | 174.4491 | 224.1427 | 197.3142 | 210.0689 | 244.1679 | 235.4592 | 262.1063 | 246.6492 | 229.3944 | 225.9725 | 178.2498 | 846514.2596
Average Power Taken at 17-22 Hours (kW) | 184.7755 | 148.2817 | 190.5213 | 167.717 | 178.5585 | 207.5427 | 200.1403 | 222.7903 | 209.6518 | 194.9853 | 192.0767 | 151.5123 | 314797.4903
Average Power Taken at 22-06 Hours (kW) | 141.2989 | 113.3919 | 145.6928 | 128.2542 | 136.5448 | 158.7091 | 153.0485 | 170.3691 | 160.322 | 149.1064 | 146.8822 | 115.8623 | 395480.8807
Max. Power can be obtained from Co-Gen btwn 06-17 Hrs (kW) | 206 | 162.2376 | 206 | 183.5022 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 165.7723 | 756963.8701
Max. Power can be obtained from Co-Gen btwn 17-22 Hrs (kW) | 171.8413 | 137.902 | 177.1848 | 155.9768 | 166.0594 | 206 | 186.1305 | 206 | 206 | 181.3363 | 178.6313 | 140.9064 | 295955.6451
Max. Power can be obtained from Co-Gen btwn 22-06 Hrs (kW) | 131.408 | 105.4545 | 135.4943 | 119.2764 | 126.9866 | 147.5995 | 142.3351 | 158.4432 | 149.0994 | 138.6689 | 136.6004 | 107.752 | 367797.219
Average Heating Need in 06-17 Hours (kW) | 282.0136 | 248.8989 | 234.2692 | 217.7349 | 136.5398 | 82.7845 | 72.0838 | 79.9626 | 105.4379 | 112.2395 | 149.5479 | 154.2618 | 600247.7951
Average Heating Need in 17-22 Hours (kW) | 238.3015 | 210.3196 | 197.9575 | 183.986 | 115.3761 | 69.9529 | 60.9108 | 67.5684 | 89.095 | 94.8423 | 126.368 | 130.3512 | 221904.1068
Average Heating Need in 22-06 Hours (kW) | 195.1534 | 172.2381 | 162.1143 | 150.6726 | 94.4855 | 57.2869 | 49.882 | 55.3341 | 72.963 | 77.6697 | 103.4871 | 106.7492 | 298548.2471
Max. Heating Pow. (kW) from Co-Gen between 06-17 Hours | 246 | 193.7401 | 234.2692 | 217.7349 | 136.5398 | 82.7845 | 72.0838 | 79.9626 | 105.4379 | 112.2395 | 149.5479 | 154.2618 | 571072.6136
Max. Heating Pow. (kW) from Co-Gen between 17-22 Hours | 205.2085 | 164.6791 | 197.9575 | 183.986 | 115.3761 | 69.9529 | 60.9108 | 67.5684 | 89.095 | 94.8423 | 126.368 | 130.3512 | 210881.413
Max. Heating Pow. (kW) from Co-Gen between 22-06 Hours | 156.9241 | 125.9311 | 161.8039 | 142.4369 | 94.4855 | 57.2869 | 49.882 | 55.3341 | 72.963 | 77.6697 | 103.4871 | 106.7492 | 277139.2901
Electricity Produced by the Co-Gen Unit (kWh/month) | 120201.6193 | 95476.8536 | 121889.5618 | 107991.0246 | 118375.2483 | 128707.8784 | 124715.3406 | 131201.9455 | 129052.8661 | 123200.9339 | 122346.4729 | 97556.9891 | 1420716.7342
Max. Amount of Electricity That Can Be Produced (kWh/month) | 142140 | 142140 | 142140 | 142140 | 142140 | 142140 | 142140 | 142140 | 142140 | 142140 | 142140 | 142140 | 1705680
Amount of Thermal Energy Can Be Produced (kWh/month) | 143541.7396 | 114016.0484 | 145557.4379 | 128960.1556 | 141360.7334 | 153699.6994 | 148931.9116 | 156678.0514 | 154111.6751 | 147123.4454 | 146103.0696 | 116500.0938 | 1696584.0612
Natural Gas Savings to Be Achieved by Heating (kWh/month) | 143541.7396 | 114016.0484 | 139895.0961 | 128193.6911 | 81577.0497 | 49460.4096 | 43067.198 | 47774.439 | 62994.9307 | 67058.5874 | 89348.8792 | 92165.2478 | 1059093.3168
Natural Gas Savings to Be Achieved by Heating (TL/month) | 152175.1227 | 120873.5955 | 148309.1503 | 135903.9589 | 86483.5385 | 52435.2285 | 45657.4943 | 50647.8544 | 66783.7894 | 71091.8567 | 94722.8082 | 97708.5685 | 1122792.9657
Co-Gen capacity utilization rate (%) | 84.5657 | 67.171 | 85.7532 | 75.9751 | 83.2807 | 90.5501 | 87.7412 | 92.3047 | 90.7928 | 86.6758 | 86.0746 | 68.6344 | 83.2933
Percentage of Meeting Electricity Needs (%) | 93.959 | 93 | 92.405 | 93 | 95.7531 | 89.5716 | 90.0032 | 85.0582 | 88.9081 | 91.2609 | 92.0003 | 93 | 91.2592
Percentage of Meeting Heating Needs (%) | 85.1921 | 76.6715 | 99.949 | 98.5439 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 94.5028
Evaluation Rate of Produced Heat (%) | 100 | 100 | 96.1099 | 99.4057 | 57.7084 | 32.1799 | 28.9174 | 30.4921 | 40.8762 | 45.5798 | 61.1547 | 79.1117 | 62.425
Cumulative Efficiency(%) | 91.3131 | 91.3131 | 89.3799 | 91.0178 | 70.2955 | 57.6086 | 55.9872 | 56.7698 | 61.9304 | 64.2679 | 72.0082 | 80.9323 | 72.6395
Amount of Electricity Received from TEDAS (kWh/month) | 7728.2698 | 7186.4298 | 10018.4382 | 8128.3567 | 5250.2843 | 14984.9071 | 13852.4011 | 23047.5955 | 16100.1652 | 11797.6829 | 10638.3664 | 7342.9992 | 136075.8963
Amount of Additona Natural Gas Received IGDAS (m3/month) | 2600.8611 | 3616.2842 | 7.4436 | 197.4567 | 1.5169e-12 | 0 | 7.5846e-13 | 7.5846e-13 | 0 | 0 | 1.5169e-12 | 1.5169e-12 | 6422.0455
Co-Gen Unit Consumption Cost (TL/month) | 306206.0397 | 243221.2592 | 310505.9667 | 275100.3202 | 301553.4747 | 327875.1978 | 317704.4598 | 334228.6765 | 328754.0324 | 313846.6044 | 311669.9189 | 248520.2733 | 3619186.2235
CK Electricity Cost (TL/month) | 29212.8599 | 27164.7048 | 37869.6963 | 30725.1883 | 19846.0747 | 56642.9488 | 52362.0762 | 87119.9111 | 60858.6246 | 44595.2415 | 40213.0252 | 27756.5369 | 514366.8882
Additional Natural Gas Cost (TL/month) | 26450.7573 | 36777.61 | 75.7014 | 2008.1344 | 1.5427e-11 | 0 | 7.7136e-12 | 7.7136e-12 | 0 | 0 | 1.5427e-11 | 1.5427e-11 | 65312.2031
Total Energy Cost (TL/month) | 361869.6568 | 307163.574 | 348451.3644 | 307833.6429 | 321399.5494 | 384518.1466 | 370066.536 | 421348.5876 | 389612.657 | 358441.8459 | 351882.9441 | 276276.8102 | 4198865.3148
TOTAL GROSS SAVINGS (TL/MONTH) | 300331.2041 | 238554.8427 | 298545.7273 | 269009.7117 | 232388.5023 | 211075.8109 | 199377.0219 | 212362.532 | 225849.591 | 222944.7826 | 245522.557 | 217953.7141 | 2873915.9975
Working Hours of the Co-Gen Unit | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 8280
Operating and Maintenance Expenses (TL/Month) | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 37524.96 | 450299.52
Years | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Depreciation (TL) | -4417338.1928 | -1993721.7153 | 429894.7622 | 2853511.2398 | 5277127.7173 | 7700744.1948 | 10124360.6724 | 12547977.1499 | 14971593.6274 | 17395210.105 | 19818826.5825 | 22242443.06
TOTAL NET SAVINGS (TL/MONTH) | 262806.2441 | 201029.8827 | 261020.7673 | 231484.7517 | 194863.5423 | 173550.8509 | 161852.0619 | 174837.572 | 188324.631 | 185419.8226 | 207997.597 | 180428.7541 | 2423616.4775
TOTAL INVESTMENT AMOUNT (TL) | [12 empty] | 4417338.1928
37.2854
INVESTMENT REFUND PERIOD (YEAR) | 0.0011628 March: 51.5752 | 1.8226

## Sayfa1 (3)
HOSPITAL COGENERATION SYSTEM ANNUAL SAVINGS ANALYSIS TABLE
Natural Gas Unit Price (TL/m3) | 13 |  | Electrical Capacity (kW) |  |  |  |  | 3200 |  | Working Hour Periods
Electrik Unit Price (TL/kWh) | 3.1 |  | Thermal Energy Capacity (kW) |  |  |  |  | 3376 |  | T1 (06-17) | 320
Exchange Rate (USD/TL) | 20 |  | Fuel Consumption (kW) |  |  |  |  | 7472 |  | T2 (17-22) | 140
Calorific Value of Natural Gas (kcal/m3) | 8250 |  | Working Hour |  |  |  |  | 690 |  | T3 (22-06) | 230
Correction Factor for Natural Gas | 0.0011628
| January | February | March | April | May | June | July | August | September | October | November | December | Total
Electric Consumption (kWh/Month) | 1790454 | 1436833 | 1846130 | 1625159 | 1730212 | 2011065 | 1939337 | 2158813 | 2031502 | 1889385 | 1861201 | 1468137 | 21788228
Natural Gas Consumption (m3/Month) | 245047 | 216273 | 203561 | 189194 | 118642 | 71933 | 62635 | 69481 | 91617 | 97527 | 129945 | 134041 | 1629896
Heating Energy Demand (kWh/Month) | 2350741.5698 | 2074711.9186 | 1952765.407 | 1814942.4419 | 1138135.4651 | 690054.9419 | 600859.0116 | 666532.8488 | 878884.0116 | 935578.7791 | 1246565.407 | 1285858.4302 | 15635630.2326
Electricity Cost (TL/Month) | 5550407.4 | 4454182.3 | 5723003 | 5037992.9 | 5363657.2 | 6234301.5 | 6011944.7 | 6692320.3 | 6297656.2 | 5857093.5 | 5769723.1 | 4551224.7 | 67543506.8
Natural Gas Cost (TL/Month) | 3185611 | 2811549 | 2646293 | 2459522 | 1542346 | 935129 | 814255 | 903253 | 1191021 | 1267851 | 1689285 | 1742533 | 21188648
Total Energy Cost (TL/Month) | 8736018.4 | 7265731.3 | 8369296 | 7497514.9 | 6906003.2 | 7169430.5 | 6826199.7 | 7595573.3 | 7488677.2 | 7124944.5 | 7459008.1 | 6293757.7 | 88732154.8
Average Power Taken at 06-17 Hours (kW) | 3042.4027 | 2441.5174 | 3137.0093 | 2761.5276 | 2940.0374 | 3417.2727 | 3295.39 | 3668.3314 | 3452 | 3210.5098 | 3162.6185 | 2494.7103 | 11847464.6729
Average Power Taken at 17-22 Hours (kW) | 2586.0423 | 2075.2898 | 2666.4579 | 2347.2985 | 2499.0318 | 2904.6818 | 2801.0815 | 3118.0816 | 2934.2 | 2728.9333 | 2688.2257 | 2120.5037 | 4405775.9252
Average Power Taken at 22-06 Hours (kW) | 1977.5618 | 1586.9863 | 2039.0561 | 1794.9929 | 1911.0243 | 2221.2273 | 2142.0035 | 2384.4154 | 2243.8 | 2086.8314 | 2055.702 | 1621.5617 | 5534987.4019
Max. Power can be obtained from Co-Gen btwn 06-17 Hrs (kW) | 2829.4345 | 2270.6112 | 2917.4187 | 2568.2207 | 2734.2348 | 3200 | 3200 | 3200 | 3200 | 3200 | 2941.2352 | 2320.0806 | 11065995.408
Max. Power can be obtained from Co-Gen btwn 17-22 Hrs (kW) | 2405.0193 | 1930.0195 | 2479.8059 | 2182.9876 | 2324.0996 | 2701.3541 | 2605.0058 | 2899.8159 | 2728.806 | 2537.908 | 2500.0499 | 1972.0685 | 4097371.6105
Max. Power can be obtained from Co-Gen btwn 22-06 Hrs (kW) | 1839.1324 | 1475.8973 | 1896.3221 | 1669.3434 | 1777.2526 | 2065.7414 | 1992.0632 | 2217.5063 | 2086.734 | 1940.7532 | 1911.8029 | 1508.0524 | 5147538.2837
Average Heating Need in 06-17 Hours (kW) | 3934.5589 | 3472.5537 | 3268.4454 | 3037.7639 | 1904.9568 | 1154.981 | 1005.6891 | 1115.6108 | 1471.0341 | 1565.9271 | 2086.4416 | 2152.2084 | 8374454.6487
Average Heating Need in 17-22 Hours (kW) | 3324.7023 | 2934.3079 | 2761.8364 | 2566.9105 | 1609.6885 | 975.9589 | 849.8073 | 942.6912 | 1243.0238 | 1323.2084 | 1763.0432 | 1818.6161 | 3095931.2029
Average Heating Need in 22-06 Hours (kW) | 2722.7148 | 2403.0071 | 2261.7642 | 2102.1326 | 1318.2301 | 799.2468 | 695.9369 | 772.0027 | 1017.9556 | 1083.6215 | 1443.8176 | 1489.3282 | 4165244.3809
Max. Heating Pow. (kW) from Co-Gen between 06-17 Hours | 2985.0534 | 2395.4948 | 3077.8767 | 2709.4728 | 1904.9568 | 1154.981 | 1005.6891 | 1115.6108 | 1471.0341 | 1565.9271 | 2086.4416 | 2152.2084 | 7559918.911
Max. Heating Pow. (kW) from Co-Gen between 17-22 Hours | 2537.2954 | 2036.1706 | 2616.1952 | 2303.0519 | 1609.6885 | 975.9589 | 849.8073 | 942.6912 | 1243.0238 | 1323.2084 | 1763.0432 | 1818.6161 | 2802625.0509
Max. Heating Pow. (kW) from Co-Gen between 22-06 Hours | 1940.2847 | 1557.0716 | 2000.6199 | 1761.1573 | 1318.2301 | 799.2468 | 695.9369 | 772.0027 | 1017.9556 | 1083.6215 | 1443.8176 | 1489.3282 | 3652232.7758
Electricity Produced by the Co-Gen Unit (kWh/month) | 1665122.22 | 1336254.69 | 1716900.9 | 1511397.87 | 1609097.16 | 1877310.0864 | 1846875.3536 | 1940000.68 | 1885981.66 | 1825680.3423 | 1730916.93 | 1365367.41 | 20310905.3022
Max. Amount of Electricity That Can Be Produced (kWh/month) | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 2208000 | 26496000
Amount of Thermal Energy Can Be Produced (kWh/month) | 1756703.9421 | 1409748.698 | 1811330.4495 | 1594524.7529 | 1697597.5038 | 1980562.1411 | 1948453.498 | 2046700.7174 | 1989710.6513 | 1926092.7611 | 1826117.3612 | 1440462.6175 | 21428005.0938
Natural Gas Savings to Be Achieved by Heating (kWh/month) | 1756703.9421 | 1409748.6979 | 1811330.4495 | 1594524.7529 | 1138135.4651 | 690054.9419 | 600859.0116 | 666532.8488 | 878884.0116 | 935578.7791 | 1246565.407 | 1285858.4302 | 14014776.7377
Natural Gas Savings to Be Achieved by Heating (TL/month) | 2380600.0088 | 1910423.084 | 2454627.2031 | 2160822.6348 | 1542346 | 935129 | 814255 | 903253 | 1191021 | 1267851 | 1689285 | 1742533 | 18992145.9307
Co-Gen capacity utilization rate (%) | 75.4131 | 60.5188 | 77.7582 | 68.451 | 72.8758 | 85.0231 | 83.6447 | 87.8623 | 85.4158 | 82.6848 | 78.393 | 61.8373 | 76.6565
Percentage of Meeting Electricity Needs (%) | 93 | 93 | 93 | 93 | 93 | 93.3491 | 95.2323 | 89.8642 | 92.8368 | 96.6283 | 93 | 93 | 93.2196
Percentage of Meeting Heating Needs (%) | 74.7298 | 67.9491 | 92.7572 | 87.8554 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 89.6336
Evaluation Rate of Produced Heat (%) | 100 | 100 | 100 | 100 | 67.0439 | 34.8414 | 30.8377 | 32.5662 | 44.1714 | 48.5739 | 68.2632 | 89.267 | 65.404
Cumulative Efficiency(%) | 88.0086 | 88.0086 | 88.0086 | 88.0086 | 73.1183 | 58.5686 | 56.7597 | 57.5406 | 62.7841 | 64.7732 | 73.6692 | 83.1592 | 72.3774
Amount of Electricity Received from TEDAS (kWh/month) | 125331.78 | 100578.31 | 129229.1 | 113761.13 | 121114.84 | 133754.9136 | 92461.6464 | 218812.32 | 145520.34 | 63704.6577 | 130284.07 | 102769.59 | 1477322.6978
Amount of Additona Natural Gas Received IGDAS (m3/month) | 61923.9224 | 69317.3782 | 14743.5228 | 22976.8742 | 0 | 0 | 0 | 1.2135e-11 | 0 | 0 | 2.4271e-11 | 2.4271e-11 | 168961.6976
Co-Gen Unit Consumption Cost (TL/month) | 5268910.92 | 4228282.3708 | 5432753.0988 | 4782484.2201 | 5091632.011 | 5940332.4846 | 5844028.5052 | 6138703.0001 | 5967771.7611 | 5776961.5805 | 5477103.7252 | 4320403.1331 | 64269366.8103
CK Electricity Cost (TL/month) | 388528.518 | 311792.761 | 400610.21 | 352659.503 | 375456.004 | 414640.2323 | 286631.1039 | 678318.1921 | 451113.054 | 197484.439 | 403880.617 | 318585.729 | 4579700.3632
Additional Natural Gas Cost (TL/month) | 805010.9912 | 901125.916 | 191665.7969 | 298699.3652 | 0 | 0 | 0 | 1.5776e-10 | 0 | 0 | 3.1552e-10 | 3.1552e-10 | 2196502.0693
Total Energy Cost (TL/month) | 6462450.4292 | 5441201.0478 | 6025029.1057 | 5433843.0883 | 5467088.015 | 6354972.7168 | 6130659.6091 | 6817021.1922 | 6418884.8151 | 5974446.0195 | 5880984.3422 | 4638988.8621 | 71045569.2429
TOTAL GROSS SAVINGS (TL/MONTH) | 2273567.9708 | 1824530.2522 | 2344266.8943 | 2063671.8117 | 1438915.185 | 814457.7832 | 695540.0909 | 778552.1078 | 1069792.3849 | 1150498.4805 | 1578023.7578 | 1654768.8379 | 17686585.5571
Working Hours of the Co-Gen Unit | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 8280
Operating and Maintenance Expenses (TL/Month) | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 401116.32 | 4813395.84
Years | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Depreciation (TL) | -37942534.0454 | -25069344.3283 | -12196154.6112 | 677035.1059 | 13550224.8231 | 26423414.5402 | 39296604.2573 | 52169793.9744 | 65042983.6916 | 77916173.4087 | 90789363.1258 | 103662552.8429
TOTAL NET SAVINGS (TL/MONTH) | 1872451.6508 | 1423413.9322 | 1943150.5743 | 1662555.4917 | 1037798.865 | 413341.4632 | 294423.7709 | 377435.7878 | 668676.0649 | 749382.1605 | 1176907.4378 | 1253652.5179 | 12873189.7171
TOTAL INVESTMENT AMOUNT (TL) | [12 empty] | 37942534.0454
INVESTMENT REFUND PERIOD (YEAR) | [12 empty] | 2.9474